## Frese PV
QUICK - CALC Frese PV
Setting & Selection program Frese PV Differential Pressure Control Valve
Input
Input ∆Ps = |  | 40 | (kPa) Differential Pessure setting
Input Q = |  | 300 | (l/h) Design flow
Dim. | ∆Ps range | Range |  | Pre-set
|  | Flow (l/h) | Range ∆Pp (kPa) | Number of turns
DN15 | 5-30 kPa | 50-600 | 5-400 | NOT POSSIBLE
DN15 | 20-60 kPa | 100-1200 | 20-400 | 8.5673
DN20 | 5-30kPa | 100-1000 | 5-400 | NOT POSSIBLE
DN20 | 20-60kPa | 150-2000 | 20-400 | 8.783
DN25 | 5-30 kPa | 600-2500 | 5-400 | NOT POSSIBLE
DN25 | 20-60 kPa | 700-4000 | 20-400 | NOT POSSIBLE
DN32 | 20-80 kPa | 1000-5000 | 20-400 | NOT POSSIBLE
DN40 | 20-80 kPa | 3000-8000 | 20-400 | NOT POSSIBLE
DN50 | 20-80 kPa | 5000-15000 | 20-400 | NOT POSSIBLE
Calculation of pressure loss
Dimension |  | ∆Pv (kPa) | Min. ∆Pp (kPa)
DN15 5-30 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN15 20-60 kPa |  | 0.69444 | 40.6944
DN20 5-30kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN20 20-60kPa |  | 0.5625 | 40.5625
DN25 5-30 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN25 20-60 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN32 20-80 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN40 20-80 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN50 20-80 kPa |  | NOT POSSIBLE | NOT POSSIBLE
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type |  | X | Y | Z | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN15 5-30 kPa |  | 5 | 494.76 | 0.5575 | 3.6 | 50 | 600 | 300 | UDEN FOR OMRÅDET
DN15 20-60 kPa |  | 20 | 747.59 | 0.3133 | 3.6 | 100 | 1200 | 300 | 40
DN20 5-30 kPa |  | 5 | 682.82 | 0.59 | 4 | 100 | 1000 | 300 | UDEN FOR OMRÅDET
DN20 20-60 kPa |  | 20 | 596.44 | 0.324 | 4 | 150 | 2000 | 300 | 40
DN25 5-30 kPa |  | 5 | 802.65 | 1.26 | 9.5 | 600 | 2500 | UDEN FOR OMRÅDET | UDEN FOR OMRÅDET
DN25 20-60 kPa |  | 20 | 1529.6 | 0.7175 | 9.5 | 700 | 4200 | UDEN FOR OMRÅDET | 40
DN32 20-80 kPa |  | 20 | 1338.84 | 0.4833 | 11.4 | 1000 | 5000 | UDEN FOR OMRÅDET | 40
DN40 20-80 kPa |  | 20 | 2213.08 | 0.4133 | 16.4 | 3000 | 8000 | UDEN FOR OMRÅDET | 40
DN50 20-80 kPa |  | 20 | 2234.42 | 0.352 | 17.9 | 5000 | 15000 | UDEN FOR OMRÅDET | 40
∆Pp = Pump pressure
∆Ps = Differential pressure setting
∆Pv = Pressure loss across valve

## Frese S
QUICK - CALC Frese S
Setting & Selection program Frese S Dynamic Balancing Valve
Input
Eingabe dP = | 20 | (kPa) Differenzdruck am Ventil
Input Q = | 25 | (l/h) Flow
Dimension | Range |  | Calculation
| Flow (l/h) | Range ∆Pp (kPa) | Pre-set | Kv | Min. ∆P (kPa)
DN15 LP | 25-804 | 8-250 | 1.0449 | 0.094228 | 8
DN15 HP | 40-1100 | 16-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN20 LP | 41-1265 | 9-250 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN20 HP | 66-1850 | 12-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN25 LP | 61-1663 | 9-250 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN25 HP | 89-2350 | 12-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN32 | 217-4800 | 14-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN40 | 175-7450 | 15-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN50 | 440-10350 | 17-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type |  |  | X | Y | Z | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN15 LP | [5 empty] | 2.2 | 25 | 804 | 25 | 20
DN15 HP | [5 empty] | 2.4 | 40 | 1100 | UDEN FOR OMRÅDET | 20
DN20 LP | [5 empty] | 3.3 | 41 | 1265 | UDEN FOR OMRÅDET | 20
DN20 HP | [5 empty] | 3.6 | 66 | 1850 | UDEN FOR OMRÅDET | 20
DN25 LP | [5 empty] | 4.1 | 61 | 1663 | UDEN FOR OMRÅDET | 20
DN25 HP | [5 empty] | 4.4 | 89 | 2350 | UDEN FOR OMRÅDET | 20
DN32 | [5 empty] | 8.8 | 217 | 4800 | UDEN FOR OMRÅDET | 20
DN40 | [5 empty] | 13.2 | 175 | 7450 | UDEN FOR OMRÅDET | 20
DN50 | [5 empty] | 16.7 | 440 | 10350 | UDEN FOR OMRÅDET | 20

## Frese OPTIMA
QUICK - CALC Frese OPTIMA
Setting & Selection program Frese OPTIMA Pressure Independent Control Valve
Input
Eingabe dP = | 20 | (kPa) Differenzdruck am Ventil
Input Q = | 2204 | (l/h) Flow
Dimension | Range |  | Calculation
| Flow (l/h) | Range ∆Pp(kPa) | Pre-set | Kv | Min. ∆P (kPa)
DN15 LF | 78-625 | 14-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN15 HF | 244-1724 | 14-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN20 LF | 131-1050 | 14-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN20 HF | 292-2039 | 13-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN25 LF | 231-1722 | 14-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN25 HF | 292-2039 | 14-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN32 | 465-3056 | 14-400 | 2.464 | 5.4061 | 16.6207
DN40 | 2022-7105 | 16-400 | 0.54367 | 5.421 | 16.5296
DN50 | 2204-8586 | 19-400 | 0.51234 | 5.2201 | 19
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type |  |  | X | Y | Z | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN15 LF | [5 empty] | 1.6 | 78 | 625 | UDEN FOR OMRÅDET | 20
DN15 HF | [5 empty] | 4.1 | 244 | 1724 | UDEN FOR OMRÅDET | 20
DN20 LF | [5 empty] | 2.6 | 131 | 1050 | UDEN FOR OMRÅDET | 20
DN20 HF | [5 empty] | 4.3 | 292 | 2039 | UDEN FOR OMRÅDET | 20
DN25 LF | [5 empty] | 4.3 | 231 | 1722 | UDEN FOR OMRÅDET | 20
DN25 HF | [5 empty] | 4.3 | 292 | 2039 | UDEN FOR OMRÅDET | 20
DN32 | [5 empty] | 7.2 | 465 | 3056 | 2204 | 20
DN40 | [5 empty] | 13.9 | 2022 | 7105 | 2204 | 20
DN50 | [5 empty] | 15.2 | 2204 | 8586 | 2204 | 20

## Frese OPTIMA Compact
QUICK - CALC Frese OPTIMA Compact
Setting & Selection program Frese OPTIMA Compact Pressure Independent Control Valve
Input
Eingabe dP = | 20 | (kPa) Differenzdruck am Ventil
Input Q = | 30 | (l/h) Flow
Dimension | Range |  | Calculation
| Flow (l/h) | Range ∆Pp(kPa) | Pre-set | Min. ∆P (kPa)
DN10 Low 2,5 | 30-182 | 14-400 | 0.5072 | 14.2703
DN10 Low 5,0 | 66-360 | 14-400 | NOT POSSIBLE | NOT POSSIBLE
DN15 Low 2,5 | 30-182 | 14-400 | 0.5072 | 14.2703
DN15 Low 5,0 | 66-360 | 14-400 | NOT POSSIBLE | NOT POSSIBLE
DN15 High 2,5 | 97-544 | 15-400 | NOT POSSIBLE | NOT POSSIBLE
DN20 High 2,5 | 97-544 | 15-400 | NOT POSSIBLE | NOT POSSIBLE
DN20 High 4,0 | 157-962 | 15-400 | NOT POSSIBLE | NOT POSSIBLE
DN20 High 5,0 | 219-1256 | 16-400 | NOT POSSIBLE | NOT POSSIBLE
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type |  |  | X | Z | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN10 Low 2,5 |  |  |  |  | 0.5 | 30 | 182 | 30 | 20
DN10 Low 5,0 |  |  |  |  | 0.9 | 66 | 360 | UDEN FOR OMRÅDET | 20
DN15 Low 2,5 |  |  |  |  | 0.5 | 30 | 182 | 30 | 20
DN15 Low 5,0 |  |  |  |  | 0.9 | 66 | 360 | UDEN FOR OMRÅDET | 20
DN15 High 2,5 |  |  |  |  | 1.3 | 97 | 544 | UDEN FOR OMRÅDET | 20
DN20 High 2,5 |  |  |  |  | 1.3 | 97 | 544 | UDEN FOR OMRÅDET | 20
DN20 High 4,0 |  |  |  |  | 2.1 | 157 | 962 | UDEN FOR OMRÅDET | 20
DN20 High 5,0 |  |  |  |  | 2.7 | 219 | 1256 | UDEN FOR OMRÅDET | 20

## Frese PVS
QUICK - CALC Frese PVS | [9 empty] | QUICK - CALC Frese S
Selection program Frese PVS Differential Pressure & Dynamic Flow Control | [9 empty] | Auslegungsprogramm für Frese S Dynamischer Volumenstromregler
| Input | [9 empty] | Eingabe
Input ∆Ps = | 20 | (kPa) Differential pressure setting | [7 empty] | Eingabe dP = | 20 | (kPa) Differenzdruck am Ventil
Input Q = | 100 | (l/h) Design flow in Zone | [7 empty] | Eingabe Q = | 25 | (l/h) Auslegungsvolumenstrom | (L/h) Auslegungsvolumenstrom
Frese PV (Return) |  | Frese S (Supply) |  |  |  | PVS System
Pre-set Frese PV |  | Pre-set Frese S |  |  |  | Total Pressure loss
Dimension | Number of turns | Dimension | Pre-set | Kv | Min. ∆P (kPa) | Min. ∆Pp (kPa)
DN15 5-30 kPa | 10.4246 | DN15 LP | 2.1991 | 0.34421 | 8.4401 | 28.5172
DN15 20-60 kPa | 2.0338 | DN15 HP | 1.6979 | 0.24578 | 16.5535 | 36.616
DN20 5-30kPa | 10.7965 | DN20 LP | 1.619 | 0.32588 | 9.4163 | 29.4788
DN20 20-60kPa | NOT POSSIBLE | DN20 HP | 1.3087 | 0.28361 | 12.4321 | NOT POSSIBLE
DN25 5-30 kPa | NOT POSSIBLE | DN25 LP | 1.2827 | 0.32995 | 9.1853 | NOT POSSIBLE
DN25 20-60 kPa | NOT POSSIBLE | DN25 HP | 1.1068 | 0.30225 | NICHT MÖGLICH | NOT POSSIBLE
DN32 20-80 kPa | NOT POSSIBLE | DN32 HP | NOT POSSIBLE | #VALUE! | NICHT MÖGLICH | NOT POSSIBLE
DN40 20-80 kPa | NOT POSSIBLE | DN40 HP | NOT POSSIBLE | #VALUE! | NICHT MÖGLICH | NOT POSSIBLE
DN50 20-80 kPa | NOT POSSIBLE | DN50 HP | NOT POSSIBLE | #VALUE! | NICHT MÖGLICH | NOT POSSIBLE
∆Pv (kPa)
0.07716
0.0625
NOT POSSIBLE
NOT POSSIBLE
NOT POSSIBLE
NOT POSSIBLE
2
Dim. ∆Ps Rang. | Frese PV ∆P - Controller |  | Frese S Flow Controller |  |  |  | Frese PV&S ∆P & Flow Controller
| Flow range (l/h) | ∆Pp range (kPa) | Flow range (l/h) |  |  | ∆Pp range (kPa) | ∆Ps range (kPa) | Flow range (l/h) | ∆Pp range (kPa)
DN15 5-30kPa | 50-600 | 5-400 | 25-804 |  |  | 8-250 | 5-30 | 50-600 | 14-250
DN15 20-60kPa | 100-1200 | 20-400 | 40-1100 |  |  | 16-400 | 20-60 | 100-1100 | 37-400
DN20 5-30 kPa | 100-1000 | 5-400 | 41-1265 |  |  | 9-250 | 5-30 | 100-1000 | 14-250
DN20 20-60kPa | 150-2000 | 20-400 | 66-1850 |  |  | 12-400 | 20-60 | 150-1850 | 33-400
DN25 5-30kPa | 600-2500 | 5-400 | 61-1663 |  |  | 9-250 | 5-30 | 600-1663 | 17-250
DN25 20-60kPa | 700-4000 | 20-400 | 89-2350 |  |  | 12-400 | 20-60 | 700-2350 | 37-400
DN32 20-80kPa | 1000-5000 | 20-400 | 217-4800 |  |  | 14-400 | 20-80 | 1000-4800 | 38-400
DN40 20-80kPa | 3000-8000 | 20-400 | 175-7450 |  |  | 15-400 | 20-80 | 3000-7450 | 45-400
DN50 20-80kPa | 5000-15000 | 20-400 | 440-10350 |  |  | 17-400 | 20-80 | 5000-10350 | 57-400 | Der Regelbereich ist definiert von Min. Pumpendruck (Min. ∆Pp) bis Max. Pumpendruck (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN | [9 empty] | ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type | X | Y | Z | Kvs | Min | Max |  | Evaluering af Flow | Evaluering af Dp | Type | X | Y | Z | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN15 5-30 kPa | 5 | 494.76 | 0.5575 | 3.6 | 50 | 600 |  | 100 | 20 | DN15 LP |  |  |  | 2.2 | 25 | 804 | 100 | 20
DN15 20-60 kPa | 20 | 747.59 | 0.3133 | 3.6 | 100 | 1200 |  | 100 | 20 | DN15 HP |  |  |  | 2.4 | 40 | 1100 | 100 | 20
DN20 5-30 kPa | 5 | 682.82 | 0.59 | 4 | 100 | 1000 |  | 100 | 20 | DN20 LP |  |  |  | 3.3 | 41 | 1265 | 100 | 20
DN20 20-60 kPa | 20 | 596.44 | 0.324 | 4 | 150 | 2000 |  | UDEN FOR OMRÅDET | 20 | DN20 HP |  |  |  | 3.6 | 66 | 1850 | 100 | 20
DN25 5-30 kPa | 5 | 802.65 | 1.26 | 9.5 | 600 | 2500 |  | UDEN FOR OMRÅDET | 20 | DN25 LP |  |  |  | 4.1 | 61 | 1663 | 100 | 20
DN25 20-60 kPa | 20 | 1529.6 | 0.7175 | 9.5 | 700 | 4200 |  | UDEN FOR OMRÅDET | 20 | DN25 HP |  |  |  | 4.4 | 89 | 2350 | 100 | 20
DN32 20-80 kPa | 20 | 1338.84 | 0.4833 | 11.4 | 1000 | 4800 |  | UDEN FOR OMRÅDET | 20 | DN32 |  |  |  | 8.8 | 217 | 4800 | UDEN FOR OMRÅDET | 20
DN40 20-80 kPa | 20 | 2213.08 | 0.4133 | 16.4 | 3000 | 7450 |  | UDEN FOR OMRÅDET | 20 | DN40 |  |  |  | 13.2 | 175 | 7450 | UDEN FOR OMRÅDET | 20
DN50 20-80 kPa | 20 | 2234.42 | 0.352 | 17.9 | 5000 | 10350 |  | UDEN FOR OMRÅDET | 20 | DN50 |  |  |  | 16.7 | 440 | 10350 | UDEN FOR OMRÅDET | 20
∆Pp = Pump pressure
∆Ps = Differential pressure setting
∆Pv = Pressure loss across valve
S
PV
Frese S (Supply)
Frese PV (Return)
Frese PV
Frese S
Date: 01-01-2010

## ALPHA
| Quick - CALC Frese ALPHA | [11 empty] | 01.06.2011
Selection program Frese ALPHA Dynamic Balancing Valve
|  |  | Input |  | CARTRIDGE SELECTION |  |  |  | Flow | Min. ΔP | Item no. | Item no. | Deviation
| Input Q = |  | 200 | (l/h) Flow | with selected Valve dimension (DN) |  |  |  | l/h | kPa | LP | HP
| ΔP range (kPa) | DN15-25 | DN25L-50 |  | Nearest higher Flow |  |  |  | 204 | 12 | 50-11400 | 49-11400 | 2%
| LP Low Press. | 7-350 | 12-350
| HP High Press. | 7-600 | 12-600 |  | Nearest lower Flow |  |  |  | 175 | 12 | 50-11370 | 49-11370 | -12.5%
[9 empty] | Plugs |  | P/T plugs
| Dimension Valve house DN | [7 empty] | ALPHA | Item no. | ALPHA | Item no.
| Input DN = |  | 20 | [5 empty] | 20 | 49-9016 | 20 | 49-9011
ALPHA Valve
| Valve | Flow
| Dimension | range
| DN | l/h
| 15 | 25-2448
| 20 | 25-2448
| 25 | 25-2448
| 25L | 674-11355
| 32 | 674-11355
| 40 | 674-11355
| 50 | 674-11355
| Alpha Regler |  | Berechnung nächst kleiner Volumenstrom |  |  |  | Berechnung nächst größer Volumenstrom |  |  |  | Alpha Ventilgehäuse Modell
| Ventil | Vol.- | Vol.- | Min. ΔP | Art.-Nr. | Art.-Nr. | Vol.- | Min. ΔP | Art.-Nr. | Art.-Nr. | Art.-Nr. | Art.-Nr. | Art.-Nr.
| Dimension | Bereich | Strom |  | LP-Einsatz | HP-Einsatz | Strom |  | LP-Einsatz | HP-Einsatz | Alpha S | Alpha FE | Alpha DM
| DN | L/h | L/h | kPa | bis 3,5 bar | bis 6,0 bar | L/h | kPa | bis 3,5 bar | bis 6,0 bar | IG/IG | IG/IG | IG/IG
| 15 | 25-2448 | 175 | 12 | 50-11370 | 49-11370 | 204 | 12 | 50-11400 | 49-11400 | 49-9006 | 49-9004 | 49-9001
| 20 | 25-2448 | 175 | 12 | 50-11370 | 49-11370 | 204 | 12 | 50-11400 | 49-11400 | 49-9016 | 49-9014 | 49-9011
| 25 | 25-2448 | 175 | 12 | 50-11370 | 49-11370 | 204 | 12 | 50-11400 | 49-11400 | 49-9026 | 49-9024 | 49-9021
| 25L | 674-11355 | 0 | 0 | 0 | 0 | 674 | 12 | 50-33073 | 49-33073 | 49-9036 | 49-9034 | 49-9031
| 32 | 674-11355 | 0 | 0 | 0 | 0 | 674 | 12 | 50-33073 | 49-33073 | 49-9046 | 49-9044 | 49-9041
| 40 | 674-11355 | 0 | 0 | 0 | 0 | 674 | 12 | 50-33073 | 49-33073 | 49-9056 | 49-9054 | 49-9051
| 50 | 674-11355 | 0 | 0 | 0 | 0 | 674 | 12 | 50-33073 | 49-33073 | 49-9066 | 49-9064 | 49-9061
| DN15-DN25 | [7 empty] | DN25L-DN50 | [7 empty] | Gehäuse sind mit Stopfen, Druckmessnippel oder Füll- und Entleerungskugelhahn
| Kleiner |  |  |  | Grosser |  |  |  | Kleiner |  |  |  | Grosser
| L/h | Min | Vare nr. |  | L/h | Min | Vare nr. |  | L/h | Min | Vare nr. |  | L/h | Min | Vare nr. |  | Der Regelbereich = S ….
|  | DP | LP | HP |  | DP | LP | HP |  | DP | LP | HP |  | DP | LP | HP
| 0 |  |  |  | 25 | 7 | 50-11150 | N/A | 0 |  |  |  | 674 | 12 | 50-33073 | 49-33073
| 25 | 7 | 50-11150 | N/A | 36 | 7 | 50-11170 | N/A | 674 | 12 | 50-33073 | 49-33073 | 861 | 12 | 50-33082 | 49-33082
| 36 | 7 | 50-11170 | N/A | 43 | 7 | 50-11190 | N/A | 861 | 12 | 50-33082 | 49-33082 | 1020 | 12 | 50-33089 | 49-33089
| 43 | 7 | 50-11190 | N/A | 55 | 7 | 50-11210 | 49-11210 | 1020 | 12 | 50-33089 | 49-33089 | 1136 | 12 | 50-33094 | 49-33094
| 55 | 7 | 50-11210 | 49-11210 | 75 | 8 | 50-11230 | 49-11230 | 1136 | 12 | 50-33094 | 49-33094 | 1190 | 12 | 50-33096 | 49-33096
| 75 | 8 | 50-11230 | 49-11230 | 84 | 9 | 50-11260 | 49-11260 | 1190 | 12 | 50-33096 | 49-33096 | 1272 | 13 | 50-33098 | 49-33098
| 84 | 9 | 50-11260 | 49-11260 | 104 | 10 | 50-11290 | 49-11290 | 1272 | 13 | 50-33098 | 49-33098 | 1349 | 13 | 50-33102 | 49-33102
| 104 | 10 | 50-11290 | 49-11290 | 114 | 10 | 50-11300 | 49-11300 | 1349 | 13 | 50-33102 | 49-33102 | 1485 | 13 | 50-33107 | 49-33107
| 114 | 10 | 50-11300 | 49-11300 | 129 | 11 | 50-11320 | 49-11320 | 1485 | 13 | 50-33107 | 49-33107 | 1567 | 14 | 50-33111 | 49-33111
| 129 | 11 | 50-11320 | 49-11320 | 154 | 11 | 50-11350 | 49-11350 | 1567 | 14 | 50-33111 | 49-33111 | 1631 | 14 | 50-33112 | 49-33112
| 154 | 11 | 50-11350 | 49-11350 | 175 | 12 | 50-11370 | 49-11370 | 1631 | 14 | 50-33112 | 49-33112 | 1815 | 14 | 50-33118 | 49-33118
| 175 | 12 | 50-11370 | 49-11370 | 204 | 12 | 50-11400 | 49-11400 | 1815 | 14 | 50-33118 | 49-33118 | 2001 | 15 | 50-33124 | 49-33124
| 204 | 12 | 50-11400 | 49-11400 | 241 | 12 | 50-11430 | 49-11430 | 2001 | 15 | 50-33124 | 49-33124 | 2044 | 16 | 50-33125 | 49-33125
| 241 | 12 | 50-11430 | 49-11430 | 279 | 12 | 50-11460 | 49-11460 | 2044 | 16 | 50-33125 | 49-33125 | 2171 | 16 | 50-33129 | 49-33129
| 279 | 12 | 50-11460 | 49-11460 | 320 | 13 | 50-11490 | 49-11490 | 2171 | 16 | 50-33129 | 49-33129 | 2271 | 17 | 50-33132 | 49-33132
| 320 | 13 | 50-11490 | 49-11490 | 350 | 13 | 50-11510 | 49-11510 | 2271 | 17 | 50-33132 | 49-33132 | 2380 | 17 | 50-33135 | 49-33135
| 350 | 13 | 50-11510 | 49-11510 | 400 | 13 | 50-11540 | 49-11540 | 2380 | 17 | 50-33135 | 49-33135 | 2498 | 18 | 50-33138 | 49-33138
| 400 | 13 | 50-11540 | 49-11540 | 477 | 14 | 50-11570 | 49-11570 | 2498 | 18 | 50-33138 | 49-33138 | 2639 | 18 | 50-33142 | 49-33142
| 477 | 14 | 50-11570 | 49-11570 | 545 | 14 | 50-11620 | 49-11620 | 2639 | 18 | 50-33142 | 49-33142 | 2871 | 19 | 50-33148 | 49-33148
| 545 | 14 | 50-11620 | 49-11620 | 615 | 14 | 50-11725 | 49-11725 | 2871 | 19 | 50-33148 | 49-33148 | 3191 | 21 | 50-33156 | 49-33156
| 615 | 14 | 50-11725 | 49-11725 | 670 | 14 | 50-11730 | 49-11730 | 3191 | 21 | 50-33156 | 49-33156 | 3407 | 22 | 50-33161 | 49-33161
| 670 | 14 | 50-11730 | 49-11730 | 736 | 14 | 50-11735 | 49-11735 | 3407 | 22 | 50-33161 | 49-33161 | 3486 | 22 | 50-33163 | 49-33163
| 736 | 14 | 50-11735 | 49-11735 | 799 | 16 | 50-11740 | 49-11740 | 3486 | 22 | 50-33163 | 49-33163 | 3634 | 20 | 50-44148 | 49-44148
| 799 | 16 | 50-11740 | 49-11740 | 870 | 19 | 50-11745 | 49-11745 | 3634 | 20 | 50-44148 | 49-44148 | 3681 | 21 | 50-44152 | 49-44152
| 870 | 19 | 50-11745 | 49-11745 | 936 | 21 | 50-11750 | 49-11750 | 3681 | 21 | 50-44152 | 49-44152 | 4088 | 21 | 50-44156 | 49-44156
| 936 | 21 | 50-11750 | 49-11750 | 1020 | 22 | 50-20700 | 49-20700 | 4088 | 21 | 50-44156 | 49-44156 | 4315 | 21 | 50-44164 | 49-44164
| 1020 | 22 | 50-20700 | 49-20700 | 1081 | 22 | 50-20740 | 49-20740 | 4315 | 21 | 50-44164 | 49-44164 | 4542 | 22 | 50-44168 | 49-44168
| 1081 | 22 | 50-20740 | 49-20740 | 1195 | 22 | 50-20770 | 49-20770 | 4542 | 22 | 50-44168 | 49-44168 | 4769 | 22 | 50-44173 | 49-44173
| 1195 | 22 | 50-20770 | 49-20770 | 1335 | 23 | 50-20820 | 49-20820 | 4769 | 22 | 50-44173 | 49-44173 | 4996 | 23 | 50-44176 | 49-44176
| 1335 | 23 | 50-20820 | 49-20820 | 1483 | 23 | 50-20860 | 49-20860 | 4996 | 23 | 50-44176 | 49-44176 | 5450 | 24 | 50-44182 | 49-44182
| 1483 | 23 | 50-20860 | 49-20860 | 1581 | 23 | 50-20880 | 49-20880 | 5450 | 24 | 50-44182 | 49-44182 | 5905 | 25 | 50-44191 | 49-44191
| 1581 | 23 | 50-20880 | 49-20880 | 1774 | 24 | 50-20920 | 49-20920 | 5905 | 25 | 50-44191 | 49-44191 | 6539 | 26 | 50-44194 | 49-44194
| 1774 | 24 | 50-20920 | 49-20920 | 1883 | 24 | 50-20940 | 49-20940 | 6539 | 26 | 50-44194 | 49-44194 | 6831 | 27 | 50-44200 | 49-44200
| 1883 | 24 | 50-20940 | 49-20940 | 2080 | 25 | 50-20990 | 49-20990 | 6831 | 27 | 50-44200 | 49-44200 | 7267 | 28 | 50-44205 | 49-44205
| 2080 | 25 | 50-20990 | 49-20990 | 2251 | 26 | 50-21030 | 49-21030 | 7267 | 28 | 50-44205 | 49-44205 | 7721 | 30 | 50-44211 | 49-44211
| 2251 | 26 | 50-21030 | 49-21030 | 2319 | 27 | 50-21060 | 49-21060 | 7721 | 30 | 50-44211 | 49-44211 | 8176 | 31 | 50-44217 | 49-44217
| 2319 | 27 | 50-21060 | 49-21060 | 2448 | 28 | 50-21090 | 49-21090 | 8176 | 31 | 50-44217 | 49-44217 | 8630 | 33 | 50-44222 | 49-44222
| 2448 | 28 | 50-21090 | 49-21090 | 2448 | 28 | 50-21090 | 49-21090 | 8630 | 33 | 50-44222 | 49-44222 | 9084 | 34 | 50-44229 | 49-44229
[9 empty] | 9084 | 34 | 50-44229 | 49-44229 | 9538 | 36 | 50-44235 | 49-44235
[9 empty] | 9538 | 36 | 50-44235 | 49-44235 | 9990 | 38 | 50-44241 | 49-44241
[9 empty] | 9990 | 38 | 50-44241 | 49-44241 | 10445 | 40 | 50-44248 | 49-44248
[9 empty] | 10445 | 40 | 50-44248 | 49-44248 | 10900 | 42 | 50-44250 | 49-44250
[9 empty] | 10900 | 42 | 50-44250 | 49-44250 | 11355 | 44 | 50-44262 | 49-44262
[9 empty] | 11355 | 44 | 50-44262 | 49-44262 | 11355 | 44 | 50-44262 | 49-44262

## ALPHA Wafer
| QUICK - CALC Frese ALPHA Flange | [14 empty] | 13.02.2011
Selection program Frese ALPHA Wafer Dynamic Balancing Valve
|  |  | Input |  | CARTRIDGE SELECTION |  |  | Flow | Min. ΔP | Qty | Vare nr. | Flow |  | Qty | Item no. | Flow | Deviation
| Input Q = |  | 189.5 | m³/h Flow | with selected Valve dimension (DN) |  |  | m³/h | kPa | Cartriges |  |  |  | Cartridges
[5 empty] | Nearest higher Flow |  |  | 189.6 | 29 | 10 | 52-55308 | 16 |  | 2 | 52-55303 | 14.8 | 0.05277%
Cartridge Type HP (High Pressure)
| AISI 304 |  |  |  | Nearest lower Flow |  |  | 177.6 | 27 | 12 | 52-55303 | 14.8 |  |  |  |  | -6.28%
ΔP range: 13 - 600 kPa
Dimension Valve house DN
| Input DN = |  | 250
| Item no. Valve house |  | 49-9133-01
|  |  | Berechnungen Nächst kleiner Volumenstrom : |  |  |  |  | Berechnungen Nächst größer Volumenstrom :
Ventil | Vol.-Ber. | Anzahl | Vol.-Str | Min ΔP | Art.-Nr. | Vol.-Strom | Ist/Soll | Vol.-Strom | Min. ΔP | Anzahl | Art.-Nr. | Vol.- | Anz | Rest | Art.-Nr. | Vol.- | Ist/Soll
Dim. | m³/h | Einsätze | m³/h | kPa |  | m³/h | Abw. | m³/h | kPa | Einsätze |  | Strom | Eins | Vol.-Str |  | Strom | Abw.
DN |  |  | Regler Komplett |  | Einsatz | Einsatz |  | Regler Komplett |  |  | Einsatz | Eins. |  | m³/h | Einsatz | Eins.
50 | 3,8 - 45,0 | 1 | 45 | 49 | 52-66407H | 45 | -76.25% | 45 | 49 | 1 | 52-66407H | 45 | 0 | 144.5 | 0 | 0 | -76.25%
65 | 3,8 - 45,0 | 1 | 45 | 49 | 52-66407H | 45 | -76.25% | 45 | 49 | 1 | 52-66407H | 45 | 0 | 144.5 | 0 | 0 | -76.25%
80 | 3,8 - 45,0 | 1 | 45 | 49 | 52-66407H | 45 | -76.25% | 45 | 49 | 1 | 52-66407H | 45 | 0 | 144.5 | 0 | 0 | -76.25%
100 | 3,8 - 90,0 | 2 | 90 | 49 | 52-66407H | 45 | -52.51% | 90 | 49 | 1 | 52-66407H | 45 | 1 | 144.5 | 52-66407H | 45 | -52.51%
125 | 3,8 - 135,0 | 3 | 135 | 49 | 52-66407H | 45 | -28.76% | 135 | 49 | 2 | 52-66407H | 45 | 1 | 99.5 | 52-66407H | 45 | -28.76%
150 | 3,8 - 180,0 | 4 | 180 | 49 | 52-66407H | 45 | -5.013% | 180 | 49 | 3 | 52-66407H | 45 | 1 | 54.5 | 52-66407H | 45 | -5.013%
200 | 3,8 - 315,0 | 7 | 185.5 | 38 | 52-66349 | 26.5 | -2.111% | 189.7 | 38 | 6 | 52-66356 | 27.7 | 1 | 23.3 | 52-66332 | 23.5 | 0.1055%
250 | 3,8 - 540,0 | 12 | 177.6 | 27 | 52-55303 | 14.8 | -6.28% | 189.6 | 29 | 10 | 52-55308 | 16 | 2 | 14.75 | 52-55303 | 14.8 | 0.05277%
300 | 3,8 - 675,0 | 15 | 187.5 | 23 | 52-55292 | 12.5 | -1.055% | 190 | 24 | 13 | 52-55298 | 13.4 | 2 | 7.65 | 52-55260 | 7.9 | 0.2639%
350 | 3,8 - 855,0 | 19 | 169.1 | 16 | 52-55269 | 8.9 | -10.77% | 190.1 | 19 | 16 | 52-55279 | 10.4 | 3 | 7.7 | 52-55260 | 7.9 | 0.3166%
400 | 3,8 - 1.170,0 | 26 | 184.6 | 14 | 52-55251 | 7.1 | -2.586% | 190.9 | 15 | 21 | 52-55260 | 7.9 | 5 | 4.72 | 52-55213 | 5 | 0.7388%
450 | 3,8 - 1.485,0 | 33 | 188.1 | 14 | 52-55227 | 5.7 | -0.7388% | 192.6 | 14 | 23 | 52-55235 | 6.2 | 10 | 4.69 | 52-55213 | 5 | 1.636%
500 | 3,8 - 1.800,0 | 40 | 184 | 14 | 52-55206 | 4.6 | -2.902% | 190 | 14 | 30 | 52-55213 | 5 | 10 | 3.95 | 52-55189 | 4 | 0.2639%
600 | 3,8 - 2.520,0 | 56 | 184 | 14 | 52-55206 | 4.6 | -2.902% | 190 | 14 | 30 | 52-55213 | 5 | 10 | 3.95 | 52-55189 | 4 | 0.2639%
800 | 3,8 - 3.825,0 | 85 | 184 | 14 | 52-55206 | 4.6 | -2.902% | 190 | 14 | 30 | 52-55213 | 5 | 10 | 3.95 | 52-55189 | 4 | 0.2639%
| '=((SVERWEIS(($D$5/$C17);$D$40:$F$84;1)*C17)) | [6 empty] | Flow > | =((SVERWEIS(($D$5/$C22);$C$38:$I$81;1)*(C22-1)))
| '=WENN($D$5/$C23<3,8;SVERWEIS(($D$5/$C22);$D$40:$F$84;1);SVERWEIS(($D$5/$C23);$D$40:$F$84;1)) | [10 empty] | Korrektion til slut :
| '=WENN($D$5/$C24<3,8;D23;SVERWEIS(($D$5/$C24);$D$40:$F$84;1)) | [10 empty] | Spalte D:H Min el slettes
DN50-DN800
|  | Kleiner |  |  |  | Grosser | [5 empty] | WENN(Prüfung;Dann_Wert; WENN(Prüfung;Dann_Wert;Sonst_Wert))
|  | L/h | m³/h | Min |  | m³/h | Min
|  |  |  | DP | Vare nr. |  | DP | Vare nr. |  |  |  | SVERWEIS(Suchkriterium;Matrix;Spalteindex;Bereich_Verweis)
0
|  |  | 0 |  |  | 3.8 | 13 | 52-55179 |  | 45 | D | '=((SVERWEIS(($D$5/$C17);$D$40:$F$84;1)*C17))
|  | 3820 | 3.8 | 13 | 52-55179 | 3.9 | 13 | 52-55184 |  | 49 | E | '=SVERWEIS(($D$5/$C17);$D$40:$F$84;2)
|  | 3931 | 3.9 | 13 | 52-55184 | 4 | 13 | 52-55189 |  | 52-66407H | F | '=SVERWEIS(($D$5/$C17);$D$40:$F$84;3)
|  | 4049 | 4 | 13 | 52-55189 | 4.2 | 13 | 52-55194 |  | 45 | G | '=SVERWEIS(($D$5/$C17);$D$40:$F$84;1)
|  | 4199 | 4.2 | 13 | 52-55194 | 4.4 | 13 | 52-55200
|  | 4399 | 4.4 | 13 | 52-55200 | 4.6 | 14 | 52-55206
|  | 4640 | 4.6 | 14 | 52-55206 | 5 | 14 | 52-55213 |  | WENN(O23<0;
|  | 4951 | 5 | 14 | 52-55213 | 5.3 | 14 | 52-55220
|  | 5310 | 5.3 | 14 | 52-55220 | 5.7 | 14 | 52-55227
|  | 5700 | 5.7 | 14 | 52-55227 | 6.2 | 14 | 52-55235 |  | DN | Art.-Nr. Gehäuse
|  | 6209 | 6.2 | 14 | 52-55235 | 6.5 | 14 | 52-55243 |  | 50 | 49-9073-01
|  | 6511 | 6.5 | 14 | 52-55243 | 7.1 | 14 | 52-55251 |  | 65 | 49-9083-01
|  | 7081 | 7.1 | 14 | 52-55251 | 7.9 | 15 | 52-55260 |  | 80 | 49-9093-01
|  | 7901 | 7.9 | 15 | 52-55260 | 8.9 | 16 | 52-55269 |  | 100 | 49-9103-01
|  | 8900 | 8.9 | 16 | 52-55269 | 10.4 | 19 | 52-55279 |  | 125 | 49-9163-01
|  | 10399 | 10.4 | 19 | 52-55279 | 11.4 | 22 | 52-55287 |  | 150 | 49-9113-01
|  | 11355 | 11.4 | 22 | 52-55287 | 12.5 | 23 | 52-55292 |  | 200 | 49-9123-01
|  | 12491 | 12.5 | 23 | 52-55292 | 13.4 | 24 | 52-55298 |  | 250 | 49-9133-01
|  | 13399 | 13.4 | 24 | 52-55298 | 14.8 | 27 | 52-55303 |  | 300 | 49-9143-01
|  | 14762 | 14.8 | 27 | 52-55303 | 16 | 29 | 52-55308 |  | 350 | 49-9153-01
|  | 15999 | 16 | 29 | 52-55308 | 17 | 34 | 52-66285 |  | 400 | 49-9173-01
|  | 17037 | 17 | 34 | 52-66285 | 18.1 | 34 | 52-66292 |  | 450 | 49-9183-01
|  | 18148 | 18.1 | 34 | 52-66292 | 18.8 | 35 | 52-66301 |  | 500 | 49-9193-01
|  | 18797 | 18.8 | 35 | 52-66301 | 19.5 | 35 | 52-66305 |  | 600 | 49-9203-01
|  | 19467 | 19.5 | 35 | 52-66305 | 20.5 | 35 | 52-66312 |  | 800 | 49-9213-01
|  | 20464 | 20.5 | 35 | 52-66312 | 21.5 | 36 | 52-66319
|  | 21527 | 21.5 | 36 | 52-66319 | 22.4 | 36 | 52-66326
|  | 22449 | 22.4 | 36 | 52-66326 | 23.5 | 36 | 52-66332
|  | 23482 | 23.5 | 36 | 52-66332 | 24.5 | 37 | 52-66338
|  | 24531 | 24.5 | 37 | 52-66338 | 25.6 | 38 | 52-66344
|  | 25621 | 25.6 | 38 | 52-66344 | 26.5 | 38 | 52-66349
|  | 26528 | 26.5 | 38 | 52-66349 | 27.7 | 38 | 52-66356
|  | 27686 | 27.7 | 38 | 52-66356 | 29.2 | 38 | 52-66362
|  | 29157 | 29.2 | 38 | 52-66362 | 30 | 39 | 52-66367
|  | 29954 | 30 | 39 | 52-66367 | 31 | 39 | 52-66373
|  | 30976 | 31 | 39 | 52-66373 | 32.3 | 40 | 52-66379
|  | 32260 | 32.3 | 40 | 52-66379 | 33.6 | 40 | 52-66385
|  | 33565 | 33.6 | 40 | 52-66385 | 35 | 40 | 52-66391
|  | 34953 | 35 | 40 | 52-66391 | 36.3 | 42 | 52-66393
|  | 36336 | 36.3 | 42 | 52-66393 | 37.7 | 43 | 52-66398
|  | 37685 | 37.7 | 43 | 52-66398 | 38.6 | 44 | 52-66400
|  | 38607 | 38.6 | 44 | 52-66400 | 41 | 46 | 52-66407
|  | 40971 | 41 | 46 | 52-66407 | 45 | 49 | 52-66407H
|  | 45000 | 45 | 49 | 52-66407H | 45 | 49 | 52-66407H
Valve | Flow | Qty
Dim. | m³/h | Cartridges
DN
50 | 3,8 - 45,0 | 1
65 | 3,8 - 45,0 | 1
80 | 3,8 - 45,0 | 1
100 | 3,8 - 90,0 | 2
125 | 3,8 - 135,0 | 3
150 | 3,8 - 180,0 | 4
200 | 3,8 - 315,0 | 7
250 | 3,8 - 540,0 | 12
300 | 3,8 - 675,0 | 15
350 | 3,8 - 855,0 | 19
400 | 3,8 - 1.170,0 | 26
450 | 3,8 - 1.485,0 | 33
500 | 3,8 - 1.800,0 | 40
600 | 3,8 - 2.520,0 | 56
800 | 3,8 - 3.825,0 | 85

## EVA
| Quick - CALC Frese EVA | [11 empty] | 01.06.2011
Selection program Frese EVA Dynamic Balancing & Control Valve On/Off
|  | Indtast |  | CARTRIDGE SELECTION |  |  |  | Flow | Min. ΔP kPa | Min. ΔP kPa | Item no. | Item no. | Deviation
| Indtast Q = | 56 | (l/h) Flow | with selected Valve dimension (DN) |  |  |  | l/h | Cartridge | total | LP | HP
| ΔP range (kPa) | DN15-25 |  | Nearest higher Flow |  |  |  | 75 | 8 | 8 | 50-11230 | 49-11230 | 33.93%
| LP Low Press. | 7-350
| HP High Press. | 7-600 |  | Nearest lower Flow |  |  |  | 55 | 7 | 7 | 50-11210 | 49-11210 | -1.786%
| Flow l/h | 25-2448
Dimension Valve house DN ; Kvs = 3,0
| Input DN = | 15
Frese EVA with Plugs
| EVA F/F | Item no.
| 15 | 48-5803
Frese EVA with P/T plugs
| EVA F/F | Item no.
| 15 | 48-5800
|  |  |  | Actuator (NC) |  | Item no.
| Male/Male |  |  | 24 V On/Off |  | 48-5515
| EVA Basic | Item no. |  | 230 V On/Off |  | 48-5518
| 15 | 48-5806
| EVA | Berechnung nächst kleiner Volumenstrom |  |  |  |  | Berechnung nächst größer Volumenstrom |  |  |  |  | EVA Ventilgehäuse
| Ventil | Vol.- | Min. ΔP | Min. ΔP | Art.-Nr. | Art.-Nr. | Vol.- | Min. ΔP | Min. ΔP | Art.-Nr. | Art.-Nr. | Art.-Nr. | Art.-Nr.
| Dimension | Strom | Einsatz | Ges. Ventil | LP-Einsatz | HP-Einsatz | Strom | Einsatz | Ges. Ventil | LP-Einsatz | HP-Einsatz | EVA S | EVA DM
| DN | L/h | kPa | kPa | bis 3,5 bar | bis 6,0 bar | L/h | kPa | kPa | bis 3,5 bar | bis 6,0 bar | IG/IG | IG/IG
| 15 | 55 | 7 | 7 | 50-11210 | 49-11210 | 75 | 8 | 8 | 50-11230 | 49-11230 | 48-5803 | 48-5800
| 20 | 55 | 7 | 7 | 50-11210 | 49-11210 | 75 | 8 | 8 | 50-11230 | 49-11230 | 48-5804 | 48-5801
| 25 | 55 | 7 | 7 | 50-11210 | 49-11210 | 75 | 8 | 8 | 50-11230 | 49-11230 | 48-5805 | 48-5802
| EVA Basic | [10 empty] | EVA Basic
| 15 | 55 | 7 | 7 | 50-11210 | 49-11210 | 75 | 8 | 8 | 50-11230 | 49-11230 | 48-5806
| DN15-DN25 | [14 empty] | Gehäuse sind mit Stopfen, Druckmessnippel oder Füll- und Entleerungskugelhahn
| Kleiner |  |  |  |  | Grosser
| L/h | Min | Min DP To |  |  | L/h | Min | Min DP To | Vare nr. | [6 empty] | Der Regelbereich = S ….
|  | DP | Geh.+Eins. | LP | HP |  | DP | Geh+Ein | LP | HP
| 0 |  |  |  |  | 25 | 7 | 7 | 50-11150 | N/A
| 25 | 7 | 7 | 50-11150 | N/A | 36 | 7 | 7 | 50-11170 | N/A
| 36 | 7 | 7 | 50-11170 | N/A | 43 | 7 | 7 | 50-11190 | N/A
| 43 | 7 | 7 | 50-11190 | N/A | 55 | 7 | 7 | 50-11210 | 49-11210
| 55 | 7 | 7 | 50-11210 | 49-11210 | 75 | 8 | 8 | 50-11230 | 49-11230
| 75 | 8 | 8 | 50-11230 | 49-11230 | 84 | 9 | 9 | 50-11260 | 49-11260
| 84 | 9 | 9 | 50-11260 | 49-11260 | 104 | 10 | 10 | 50-11290 | 49-11290
| 104 | 10 | 10 | 50-11290 | 49-11290 | 114 | 10 | 10 | 50-11300 | 49-11300
| 114 | 10 | 10 | 50-11300 | 49-11300 | 129 | 11 | 11 | 50-11320 | 49-11320
| 129 | 11 | 11 | 50-11320 | 49-11320 | 154 | 11 | 11 | 50-11350 | 49-11350 |  |  |  | 50-33112 | 49-33112
| 154 | 11 | 11 | 50-11350 | 49-11350 | 175 | 12 | 12 | 50-11370 | 49-11370 |  |  |  | 50-33118 | 49-33118
| 175 | 12 | 12 | 50-11370 | 49-11370 | 204 | 12 | 12 | 50-11400 | 49-11400 |  |  |  | 50-33124 | 49-33124
| 204 | 12 | 12 | 50-11400 | 49-11400 | 241 | 12 | 13 | 50-11430 | 49-11430 |  |  |  | 50-33125 | 49-33125
| 241 | 12 | 13 | 50-11430 | 49-11430 | 279 | 12 | 13 | 50-11460 | 49-11460 |  |  |  | 50-33129 | 49-33129
| 279 | 12 | 13 | 50-11460 | 49-11460 | 320 | 13 | 14 | 50-11490 | 49-11490 |  |  |  | 50-33132 | 49-33132
| 320 | 13 | 14 | 50-11490 | 49-11490 | 350 | 13 | 14 | 50-11510 | 49-11510 |  |  |  | 50-33135 | 49-33135
| 350 | 13 | 14 | 50-11510 | 49-11510 | 400 | 13 | 15 | 50-11540 | 49-11540 |  |  |  | 50-33138 | 49-33138
| 400 | 13 | 15 | 50-11540 | 49-11540 | 477 | 14 | 17 | 50-11570 | 49-11570 |  |  |  | 50-33142 | 49-33142
| 477 | 14 | 17 | 50-11570 | 49-11570 | 545 | 14 | 17 | 50-11620 | 49-11620 |  |  |  | 50-33148 | 49-33148
| 545 | 14 | 17 | 50-11620 | 49-11620 | 615 | 14 | 18 | 50-11725 | 49-11725 |  |  |  | 50-33156 | 49-33156
| 615 | 14 | 18 | 50-11725 | 49-11725 | 670 | 14 | 19 | 50-11730 | 49-11730 |  |  |  | 50-33161 | 49-33161
| 670 | 14 | 19 | 50-11730 | 49-11730 | 736 | 14 | 20 | 50-11735 | 49-11735 |  |  |  | 50-33163 | 49-33163
| 736 | 14 | 20 | 50-11735 | 49-11735 | 799 | 16 | 23 | 50-11740 | 49-11740 |  |  |  | 50-44148 | 49-44148
| 799 | 16 | 23 | 50-11740 | 49-11740 | 870 | 19 | 27 | 50-11745 | 49-11745 |  |  |  | 50-44152 | 49-44152
| 870 | 19 | 27 | 50-11745 | 49-11745 | 936 | 21 | 31 | 50-11750 | 49-11750 |  |  |  | 50-44156 | 49-44156
| 936 | 21 | 31 | 50-11750 | 49-11750 | 1020 | 22 | 34 | 50-20700 | 49-20700 |  |  |  | 50-44164 | 49-44164
| 1020 | 22 | 34 | 50-20700 | 49-20700 | 1081 | 22 | 35 | 50-20740 | 49-20740 |  |  |  | 50-44168 | 49-44168
| 1081 | 22 | 35 | 50-20740 | 49-20740 | 1195 | 22 | 38 | 50-20770 | 49-20770 |  |  |  | 50-44173 | 49-44173
| 1195 | 22 | 38 | 50-20770 | 49-20770 | 1335 | 23 | 43 | 50-20820 | 49-20820 |  |  |  | 50-44176 | 49-44176
| 1335 | 23 | 43 | 50-20820 | 49-20820 | 1483 | 23 | 47 | 50-20860 | 49-20860 |  |  |  | 50-44182 | 49-44182
| 1483 | 23 | 47 | 50-20860 | 49-20860 | 1581 | 23 | 51 | 50-20880 | 49-20880 |  |  |  | 50-44191 | 49-44191
| 1581 | 23 | 51 | 50-20880 | 49-20880 | 1774 | 24 | 59 | 50-20920 | 49-20920 |  |  |  | 50-44194 | 49-44194
| 1774 | 24 | 59 | 50-20920 | 49-20920 | 1883 | 24 | 61 | 50-20940 | 49-20940 |  |  |  | 50-44200 | 49-44200
| 1883 | 24 | 61 | 50-20940 | 49-20940 | 2080 | 25 | 73 | 50-20990 | 49-20990 |  |  |  | 50-44205 | 49-44205
| 2080 | 25 | 73 | 50-20990 | 49-20990 | 2251 | 26 | 82 | 50-21030 | 49-21030 |  |  |  | 50-44211 | 49-44211
| 2251 | 26 | 82 | 50-21030 | 49-21030 | 2319 | 27 | 87 | 50-21060 | 49-21060 |  |  |  | 50-44217 | 49-44217
| 2319 | 27 | 87 | 50-21060 | 49-21060 | 2448 | 28 | 95 | 50-21090 | 49-21090 |  |  |  | 50-44222 | 49-44222
| 2448 | 28 | 95 | 50-21090 | 49-21090 | 2448 | 28 | 95 | 50-21090 | 49-21090 |  |  |  | 50-44229 | 49-44229
[14 empty] | 50-44235 | 49-44235
[14 empty] | 50-44241 | 49-44241
[14 empty] | 50-44248 | 49-44248
[14 empty] | 50-44250 | 49-44250
[14 empty] | 50-44262 | 49-44262
[14 empty] | 50-44262 | 49-44262
EVA
| Valve | Flow
Dimension
| DN | l/h
| 15 | 55
| 20 | 55
| 25 | 55
EVA Basic
| 15 | 55